## Sheet1
Format for Commercial Pre-Bid Queries
Tender No : | NIT No.: TPNODL/OT/2021-22/160 Dtd. 29.01.2022
Package Name | Rate Contract for SITC (Supply, Installation, Testing & Commissioning) of various types of Jointing Kits (11kV, 33kV & LT) works in PAN TPNODL
Note : | The said format to be used only for Technical Pre-Bid Query. Any Commercial Query has to be strictly in Format B2 Format for Commercial Pre-Bid Query and sent seperately
Format to be used for query regarding Technical Pre-Qualifcation Requirement, Safety Pre-Qualifcation Requirement, Technical Set of Documnt
Pre-Bid Query has to be sent in editable Excel file fomat only
Pre-Bid Query has to be sent through e-mail in E-Tender System
Reply of Pre -Bid Queries
| Specification | Clause | Particular | Proposed TPNODL Reply
1 | ENG-LV-009 | 4.0 | Cable construction for individual sizes of cable is not defined. Requesting you to please guide which type of cable should be considered for different sizes in terms of Armored/ Unarmoured, Screened (CWS or CTS)/ Unscreeened, Conductor shape- Sector/round. For LT AB cable, we request for suggested cable GTP as well. | For 4 core and 3.5 core 1.1KV Cable, please consider A2XWY (Aluminium conductor stranded sector shaped, XLPE insulation, PVC inner sheath, GI round wire armour, PVC outer sheath) & A2XFY. For LT AB Cable, please consider A2X Aluminium Conductor, Stranded Circular Compacted, XLPE insulation.
2 | ENG-LV-009 | 5.0 | Termination Table: lug: In the specification, it is mentioned that " Dimensions shall be as Annexure-I of this specification."However, we could not find the annexure-1. Request you to please share this annexure covering all the cable sizes. | Refer Annex-1 for recommended dimension of lug.
3 | ENG-LV-009 | 5.0 | Termination Table: Tinned copper braid: In the specification it is mentioned that "Size and length is as follows: 25 mm2 x 500 mm x 1 Run for 300 mm2 cables". Please clarify about other cable sizes including LT AB cables as well. | Refer Annex-4. We have mentioned recommeded earthing for all the BOQ items.
4 | ENG-LV-009 | 5.0 | Joint Table: Ferrule: In the specification, it is mentioned that " Dimensions shall be as Annexure-I of this specification."However, we could not find the annexure-1. Request you to please share this annexure covering all the cable sizes. | Refer Annex-1 for recommended dimension of Ferrule.
5 | ENG-HV-029 | 4.0 | Cable construction for individual sizes of cable is not defined.We are considering Armoured cable as per the details specified in the component table. Kindly confirm. | For HT AB Cable, please consider following construction: a) A2XCY- (Aluminium stranded compacted conductor, XLPE insulation, copper tape screen, PVC sheath) b) A2XC2Y- (Aluminium stranded compacted conductor, XLPE insulation, copper tape screen, HDPE sheath) c) A2XWaY- (Aluminium stranded compacted conductor, XLPE insulation, Aluminium wire screen, PVC sheath)
6 | ENG-HV-029 | 5.0 | Compression Lugs: Please share Annex-1 mentioned in the specification. | Refer Annex-2 for recommended dimension of lug.
7 | ENG-HV-029 | 5.0 | Compression Ferrule: Please share Annex-1 mentioned in the specification. | Refer Annex-2 for recommended dimension of ferrule.
8 | ENG-HV-023 | 4.0 | Cable construction for individual sizes of cable is not defined.kindly share. | For 3 core cable , please consider either of the following construction: A2XCWY- (Aluminum stranded compacted conductor, XLPE insulation, copper tape screen, wire GI armour, PVC sheath) For 1 core cable, please consider following construction: A2XCWaY (Aluminum conductor, XLPE insulation, copper tape screen, wire Aluminum armour, PVC sheath)
9 | ENG-HV-023 | 5.0 | Compression Lugs/ Tinned coated Mechanical Lugs: Please share Annex-1 mentioned in the specification. It is not defined which item shall be considered with mechanical lug and which item shall be considered with compression lug. Please specify. | Refer Annex-2 for recommended dimension of compression lug & ferrule. Refer Annex-4 where we have defined which item should be supplied with compression lug/ferrule and which item should be supplied with mechanical lug/ferrule.
10 | ENG-HV-023 | 5.0 | Compression Lugs/ Tinned coated Mechanical Lugs: Please share Annex-1 mentioned in the specification. It is not defined which item shall be considered with mechanical lug and which item shall be considered with compression lug. Please specify. | Refer Annex-2 for recommended dimension of compression lug & ferrule. Refer Annex-4 where we have defined which item should be supplied with compression lug/ferrule and which item should be supplied with mechanical lug/ferrule.
11 | ENG-HV-023 | 5.0 | Termination: Tinned coated copper braid: Single core armoured cable is understood to be using armour fold back earthing arrangement. However, it is not clearly covered in the clause. Qty of copper braid for 3C cable below 95 SQMM is also not covered. Kindly define. | Refer Annex-4. We have mentioned recommeded earthing for all the BOM items.
12 | ENG-HV-023 | 5.0 | Ferrules/ Mechanical Connectors: Please share Annex-1 mentioned in the specification. It is not defined which item shall be considered with mechanical connector and which item shall be considered with compression ferrule. Please specify. | Refer Annex-2 for recommended dimension of compression lug & ferrule. Refer Annex-4 where we have defined which item should be supplied with compression lug/ferrule and which item should be supplied with mechanical lug/ferrule.
13 | ENG-HV-023 | 5.0 | Tinned coated copper braid: In the specification it is mentioned that size of tinned copper braid shall be: 50 mm2 x 1 Run for 150-400 sq.mm. three core cables. Please define for other sizes as well. Similarly, 1Cx185, 1Cx 300 is not covered in the specification. Please specify. | Refer Annex-4. We have mentioned recommeded earthing for all the BOM items.
14 | ENG-EHV-015 | 4.0 | Cable construction for individual sizes of cable is not defined.kindly share. | For 3 core cable , please consider either of the following construction: A2XCWY- (Aluminum stranded compacted conductor, XLPE insulation, copper tape screen, wire GI armour, PVC sheath) A2XCFY- (Aluminum stranded compacted conductor, XLPE insulation, copper tape screen, Flat wire GI armour, PVC sheath) For 1 core cable, please consider following construction: A2XCWaY (Aluminum conductor, XLPE insulation, copper tape screen, wire Aluminum armour, PVC sheath)
15 | ENG-EHV-015 | 5.0 | Tinned coated Mechanical Lugs: Please share Annex-1 mentioned in the specification. | Please refer Annex-3 for mechanical lug/mechanical connector dimension.
16 | ENG-EHV-015 | 5.0 | Termination: Tinned coated copper braid: Defined qty is not covering complete BOQ. Please share for remaining line items as well. E.g. 3C 185, 3Cx95, 3Cx70, 3Cx35 SQMM etc. | Please refer Annex - 4
17 | ENG-EHV-015 | 5.0 | Mechanical Connectors: Please share Annex-1 mentioned in the specification. | Please refer Annex-3 for mechanical lug/mechanical connector dimension.
18 | ENG-EHV-015 | 5.0 | Termination: Tinned coated copper braid: Defined qty is not covering complete BOQ. Please share for remaining line items as well. E.g. 3C 185, 3Cx95, 3Cx70, 3Cx35 SQMM etc. | Please refer Annex-4 .

## Annex-1
1 | Aluminum Ferrule Dimension for LT ABC and 1.1 kV Cable
2 | Aluminum Lug Dimension for 1.1 KV Cable
3 | Aluminum Lug dimension for LT AB cable

## Annex-2
Aluminum Lug Dimension for 11 kV Cable
Aluminum ferrule Dimension for 11 kV Cable

## Annex-3
Mechanical Lug for 33 kV
Mechanical Connector

## Annex-4
SL No | Customer Description |  | Qty | TPNODL Requirement: Crimping/ Mechanical | TPNODL Requirement for Earthing: Tinned Copper Braid or Earthing ferrule/Lug size
1 | JT. KIT ST.TH 1.1KV XLPE 4X50 HS | EA | 50 | Crimping | 10SQMM
1 | JT. KIT ST.TH 1.1KV XLPE 4X95 HS | EA | 1000 | Crimping | 25SQMM
2 | JT. KIT ST.TH.1.1KV XLPE 4X120 HS | EA | 1000 | Crimping | 25SQMM
2 | JT. KIT ST.TH.1.1KV XLPE 4X150 HS | EA | 1000 | Crimping | 25 SQMM
3 | JT. KIT ST.TH.1.1KV XLPE 4X240 HS | EA | 200 | Crimping | 50 SQMM
4 | JT. KIT ST.TH.1.1KV XLPE 4X300 HS | EA | 500 | Crimping | 50 SQMM
5 | JT. KIT ST.TH.1.1KV XLPE 4X400 HS | EA | 200 | Crimping | 50 SQMM
6 | JT. KIT O/D 1.1KV XLPE 4X50 HS | EA | 50 | Crimping | 25 SQMM
7 | JT. KIT O/D 1.1KV XLPE 4X95 HS | EA | 100 | Crimping | 25 SQMM
8 | JT. KIT O/D 1.1KV XLPE 4X120 HS | EA | 50 | Crimping | 25 SQMM
9 | JT. KIT O/D 1.1KV XLPE 4X150 HS | EA | 100 | Crimping | 25 SQMM
10 | JT. KIT O/D 1.1KV XLPE 4X240 HS | EA | 50 | Crimping | 25 SQMM
11 | JT. KIT O/D 1.1KV XLPE 4X300 HS | EA | 100 | Crimping | 25 SQMM
12 | JT. KIT O/D 1.1KV XLPE 4X400 HS | EA | 50 | Crimping | 25 SQMM
13 | JT. KIT ST.TH 1.1KV XLPE 3.5X120 HS -XLPE | EA | 500 | Crimping | 25 SQMM
14 | JT. KIT ST.TH 1.1KV XLPE 3.5X185 HS - XLPE | EA | 500 | Crimping | 25 SQMM
15 | JT. KIT ST.TH 1.1KV XLPE 3.5X150 HS -XLPE | EA | 500 | Crimping | 25 SQMM
17 | JT. KIT ST.TH 1.1KV XLPE 3.5X120 HS -PVC | EA | 50 | Crimping | 25 SQMM
18 | JT. KIT ST.TH 1.1KV XLPE 3.5X300 HS - XLPE | EA | 500 | Crimping | 50 SQMM
19 | JT. KIT O/D 1.1KV XLPE 3.5X120 HS -XLPE | EA | 50 | Crimping | 25 SQMM
20 | JT. KIT SO/D 1.1KV XLPE 3.5X185 HS -XLPE | EA | 100 | Crimping | 25 SQMM
21 | JT. KIT O/D 1.1KV XLPE 3.5X150 HS - XLPE | EA | 50 | Crimping | 25 SQMM
23 | JT. KIT O/D 1.1KV XLPE 3.5X120 HS -PVC | EA | 100 | Crimping | 25 SQMM
24 | JT. KIT O/D 1.1KV XLPE 3.5X300 HS -XLPE | EA | 100 | Crimping | 25 SQMM
25 | JT. KIT ST.TH LTABC - 1 X 25 + 1 X 16 mm Sqr. AB. Cable. | EA | 500 | Crimping | NA
26 | JT. KIT O/D LTABC -1 X 25 + 1 X 16 mm Sqr. AB. Cable. | EA | 50 | Crimping | NA
27 | JT. KIT ST.TH LTABC -1 X 35 + 1 X 25 mm Sqr. A.B. Cable. | EA | 1000 | Crimping | NA
28 | JT. KIT O/D LTABC1 X 35 + 1 X 25 mm Sqr. A.B. Cable. | EA | 50 | Crimping | NA
29 | JT. KIT ST.TH LTABC -3 X 95 + 1 X 70 + 1 X 16 mm Sqr. A.B. Cable. | EA | 500 | Crimping | NA
30 | JT. KIT O/D LTABC 3 X 95 + 1 X 70 + 1 X 16 mm Sqr. A.B. Cable. | EA | 500 | Crimping | NA
31 | JT. KIT ST.TH LTABC -3 X 50 + 1 X 35 + 1 X 16 mm Sqr. A.B. Cable. | EA | 3000 | Crimping | NA
32 | JT. KIT O/D LTABC 3 X 50 + 1 X 35 + 1 X 16 mm Sqr. A.B. Cable. | EA | 100 | Crimping | NA
33 | JT. KIT ST.TH LTABC - 3x35+1x25+1x16 sqmm AB Cable | EA | 1000 | Crimping | NA
34 | JT. KIT O/D LTABC - 3x35+1x25+1x16 sqmm AB Cable | EA | 50 | Crimping | NA
35 | JT. KIT ST.TH LTABC -4 X 50 + 1 X 35 + 1 X 16 mm Sqr. A.B. Cable. | EA | 1000 | Crimping | NA
36 | JT. KIT O/D LTABC -4 X 50 + 1 X 35 + 1 X 16 mm Sqr. A.B. Cable. | EA | 100 | Crimping | NA
37 | JT. KIT ST.TH LTABC -4 X 70 + 1 X 50 +1 X 16 mm Sqr. A.B. Cable. | EA | 1000 | Crimping | NA
38 | JT. KIT O/D LTABC - 4 X 70 + 1 X 50 + 1X 16 mm Sqr. A.B. Cable. | EA | 100 | Crimping | NA
39 | JT. KIT ST.TH LTABC -4 X 95 + 1 X 70 +1 X 16 mm Sqr. A.B. Cable. | EA | 500 | Crimping | NA
40 | JT. KIT O/D LTABC 4 X 95 + 1 X 70 + 1 X16 mm Sqr. A.B. Cable. | EA | 80 | Crimping | NA
1 | JT. KIT ST.TH. 11KV XLPE 3 X35 HS | EA | 50 | Crimping | 25 SQMM
2 | JT. KIT O/D 11KV XLPE 3X35 HS | EA | 100 | Crimping | 25 SQMM
3 | JT. KIT I/D 11KV XLPE 3X35 HS | EA | 100 | Crimping | 25 SQMM
4 | JT. KIT ST.TH. 11KV XLPE 3 X50 HS | EA | 50 | Crimping | 25 SQMM
5 | JT. KIT O/D 11KV XLPE 3X50 HS | EA | 100 | Crimping | 25 SQMM
6 | JT. KIT I/D 11KV XLPE 3X50 HS | EA | 100 | Crimping | 25 SQMM
7 | JT. KIT ST.TH. 11KV XLPE 3 X70 HS | EA | 50 | Crimping | 25 SQMM
8 | JT. KIT O/D 11KV XLPE 3X70 HS | EA | 100 | Crimping | 25 SQMM
9 | JT. KIT I/D 11KV XLPE 3X70 HS | EA | 100 | Crimping | 25 SQMM
10 | JT. KIT ST.TH. 11KV XLPE 3 X95 HS | EA | 100 | Crimping | 50 SQMM
11 | JT. KIT O/D 11KV XLPE 3X95 HS | EA | 200 | Crimping | 25 SQMM
12 | JT. KIT I/D 11KV XLPE 3X95 HS | EA | 100 | Crimping | 25 SQMM
13 | JT. KIT ST.TH. 11KV XLPE 3 X120 HS | EA | 100 | Crimping | 50 SQMM
14 | JT. KIT O/D 11KV XLPE 3X120 HS | EA | 200 | Crimping | 25 SQMM
15 | JT. KIT I/D 11KV XLPE 3X120 HS | EA | 50 | Crimping | 25 SQMM
16 | JT. KIT ST.TH. 11KV XLPE 3 X150 HS | EA | 100 | Crimping | 50 SQMM
17 | JT. KIT O/D 11KV XLPE 3X150 HS | EA | 200 | Crimping | 50 SQMM
18 | JT. KIT I/D 11KV XLPE 3X150 HS | EA | 50 | Crimping | 50 SQMM
19 | JT. KIT ST.TH. 11KV XLPE 3 X185 HS | EA | 200 | Crimping | 50 SQMM
20 | JT. KIT O/D 11KV XLPE 3X185 HS | EA | 600 | Crimping | 50 SQMM
21 | JT. KIT I/D 11KV XLPE 3X185 HS | EA | 200 | Crimping | 50 SQMM
22 | JT. KIT ST.TH. 11KV XLPE 1 X185 HS | EA | 200 | Crimping | Ferrule-2X150
23 | JT. KIT O/D 11KV XLPE 1X185 HS | EA | 600 | Crimping | 50 SQMM+3 Lug X 150
24 | JT. KIT I/D 11KV XLPE 1X185 HS | EA | 100 | Crimping | 50 SQMM+3 Lug X 150
25 | JT. KIT ST.TH.11KV XLPE 3X300 HS | EA | 200 | Crimping | 50 SQMM
26 | JT. KIT O/D 11KV XLPE 3X300 HS | EA | 800 | Crimping | 50 SQMM
27 | JT. KIT I/D 11KV XLPE 3X300 HS | EA | 400 | Crimping | 50 SQMM
28 | JT. KIT ST.TH.11KV XLPE 1X300 HS | EA | 100 | Crimping | Ferrule-2-150
29 | JT. KIT O/D 11KV XLPE 1X300 HS | EA | 600 | Crimping | 50 SQMM+3 Lug X150
30 | JT. KIT I/D 11KV XLPE 1X300 HS | EA | 200 | Crimping | 50 SQMM+3 Lug X150
31 | JT. KIT ST.TH.11KV XLPE 1X400 HS | EA | 50 | Crimping | Ferrule-2-150
32 | JT. KIT O/D 11KV XLPE 1X400 HS | EA | 50 | Crimping | 50 SQMM+3 Lug X150
33 | JT. KIT I/D 11KV XLPE 1X400 HS | EA | 50 | Crimping | 50 SQMM+3 Lug X150
34 | JT. KIT ST.TH.11KV XLPE 1X630 HS | EA | 50 | Crimping | Ferrule-2-150
35 | JT. KIT O/D 11KV XLPE 1X630 HS | EA | 20 | Crimping | 70 SQMM+3 Lug X150
36 | JT. KIT I/D 11KV XLPE 1X630 HS | EA | 20 | Crimping | 70 SQMM+3 Lug X150
37 | JT. KIT ST.TH.11KV XLPE 1X1000 HS | EA | 10 | Crimping | Ferrule-2-185
38 | JT. KIT O/D 11KV XLPE 1X1000 HS | EA | 10 | Crimping | 70 SQMM+3 Lug X150
39 | JT. KIT I/D 11KV XLPE 1X1000 HS | EA | 10 | Crimping | 70 SQMM+3 Lug X150
40 | JT. KIT I/D 11KV XLPE 1CX630 HS (RMU) | EA | 10 | Mechanical | 70 SQMM+3 Lug X150
41 | JT. KIT I/D 11KV XLPE 3CX300/400 HS (RMU) | EA | 50 | Mechanical | 50 SQMM
42 | JT. KIT ST.TH. CABLE AB 11KV 3X95+1X95 XLPE HS | EA | 1000 | Crimping | Ferrule
43 | JT. KIT O/D CABLE AB 11KV 3X95+1X95 XLPE HS | EA | 1000 | Crimping | 25 SQMM
44 | JT. KIT ST.TH. CABLE AB 11KV 3X150+1X150 XLPE HS | EA | 80 | Crimping | Ferrule
45 | JT. KIT O/D CABLE AB 11KV 3X150+1X150 XLPE HS | EA | 80 | Crimping | 25 SQMM
1 | JT. KIT O/D 33KV XLPE 3X300 HS | EA | 500 | Mechanical | 70 SQMM
2 | JT. KIT I/D 33KV XLPE 3X300 HS | EA | 200 | Mechanical | 70 SQMM
3 | JT. KIT ST.TH.33KV XLPE 3X 300 HS | EA | 200 | Mechanical | 70 SQMM
4 | JT. KIT ST.TH.33KV XLPE 3X 400 HS | EA | 100 | Mechanical | 70 SQMM
5 | JT. KIT O/D 33KV XLPE 3X400 HS | EA | 200 | Mechanical | 70 SQMM
6 | JT. KIT I/D 33 KV XLPE 3X400 HS | EA | 50 | Mechanical | 70 SQMM
7 | JT. KIT O/D 33KV XLPE 1X300 HS | EA | 400 | Mechanical | 50 SQMM+3X150 Lug
8 | JT. KIT I/D 33KV XLPE 1X300 HS | EA | 200 | Mechanical | 50 SQMM+3X150 Lug
9 | JT. KIT ST.TH.33KV XLPE 1X 300 HS | EA | 200 | Mechanical | 2 Ferrule-150
10 | JT. KIT ST.TH.33KV XLPE 1X 400 HS | EA | 100 | Mechanical | 2 Ferrule-150
11 | JT. KIT O/D 33KV XLPE 1X400 HS | EA | 100 | Mechanical | 50 SQMM+3X150 Lug
12 | JT. KIT I/D 33 KV XLPE 1X400 HS | EA | 100 | Mechanical | 50 SQMM+3X150 Lug
13 | JT. KIT ST.TH.33KV XLPE 3X 185 HS | EA | 200 | Mechanical | 70 SQMM
14 | JT. KIT O/D 33KV XLPE 3X185 HS | EA | 400 | Mechanical | 70 SQMM
15 | JT. KIT I/D 33 KV XLPE 3X185 HS | EA | 200 | Mechanical | 70 SQMM
16 | JT. KIT ST.TH.33KV XLPE 1X 185 HS | EA | 10 | Mechanical | 2 FerruleX150
17 | JT. KIT O/D 33KV XLPE 1X185 HS | EA | 100 | Mechanical | 50 SQMM+3X150 Lug
18 | JT. KIT I/D 33 KV XLPE 1X185 HS | EA | 100 | Mechanical | 50 SQMM+3X150 Lug
19 | JT. KIT ST.TH.33KV XLPE 3X 95 HS | EA | 50 | Mechanical | 70 SQMM
20 | JT. KIT O/D 33KV XLPE 3X95 HS | EA | 100 | Mechanical | 70 SQMM
21 | JT. KIT I/D 33 KV XLPE 3X95 HS | EA | 50 | Mechanical | 70 SQMM
22 | JT. KIT ST.TH.33KV XLPE 3X 70 HS | EA | 50 | Mechanical | 70 SQMM
23 | JT. KIT O/D 33KV XLPE 3X70 HS | EA | 100 | Mechanical | 70 SQMM
24 | JT. KIT I/D 33 KV XLPE 3X70 HS | EA | 50 | Mechanical | 70 SQMM
25 | JT. KIT ST.TH.33KV XLPE 3X 35 HS | EA | 50 | Mechanical | 70 SQMM
26 | JT. KIT O/D 33KV XLPE 3X35 HS | EA | 100 | Mechanical | 70 SQMM
27 | JT. KIT I/D 33 KV XLPE 3X35 HS | EA | 20 | Mechanical | 70 SQMM
28 | JT. KIT TRM. GIS F/33KV 400 SQMM XLPE | EA | 20 |  | 70 SQMM
29 | JT. KIT TRM.AIS I/D 33KV XLPE 3X400 RSTI | EA | 10 |  | 70 SQMM
30 | JT. KIT I/D Screened 33 KV XLPE 1CX630 HS (RMU) | EA | 10 |  | 70 SQMM